## Survey Data
Feeder: | 803634 |  |  | Substation: | SEABOARD |  | Wind Zone: | 145 |  | Hardening Level: |  |  | Extreme Wind |  |  |  | SURVEY DATA | [65 empty] | Transmission Windloading Form
Pole Data | [8 empty] | Circuit 1 | Circuit 1 | Pull Off 1 | Pull Off 2 | Pull Off | Equipment | [6 empty] | Attachment Data | [25 empty] | Conductor Data | [5 empty] | Asset Data |  | GPS Coordinate |  | Guying Data
FPL ID | Pole Number | Pole Type | Owner | Access (Y/N) | Utility Pole Owner - Action Taken | Pole Height | Pole Class | Framing | Span Length (1) | Span Length (2) | Span Length (1) | Span Length (2) | Framing | Equip Type | Equip Quan. | Streetlight | Riser Type 1 | Riser Type 2 | No CATV Attachments | Total Size CATV | CATV 1 Attach Height | CATV 1 Attach Diameter | CATV 2 Attach Height | CATV 2 Attach Diameter | CATV 3 Attach Height | CATV 3 Attach Diameter | CATV 4 Attach Height | CATV 4 Attach Diameter | CATV 5 Attach Height | CATV 5 Attach Diameter | CATV 6 Attach Height | CATV 6 Attach Diameter | No Telecom Attached | Total Size Telecom | TELCO 1 Attach Height | TELCO 1 Attach Diameter | TELCO 2 Attach Height | TELCO 2 Attach Diameter | TELCO 3 Attach Height | TELCO 3 Attach Diameter | TELCO 4 Attach Height | TELCO 4 Attach Diameter | TELCO 5 Attach Height | TELCO 5 Attach Diameter | TELCO 6 Attach Height | TELCO 6 Attach Diameter | # of Phases | Primary Wire Type | Neutral Wire Type | Open Wire Type | # of Open Wires | Multiplex Type | Switch Number | TLN Coordinate | Latitude | Longitude | Guy 1 Assc. | Guy 1 Lead Length | Guy 1 Diameter | Guy 1 Bearing | Guy 2 Assc. | Guy 2 Lead Length | Guy 2 Diameter | Guy 2 Bearing | Guy 3 Assc. | Guy 3 Lead Length | Guy 3 Diameter | Guy 3 Bearing | Guy 4 Assc. | Guy 4 Lead Length | Guy 4 Diameter | Guy 4 Bearing | Guy 5 Assc. | Guy 5 Lead Length | Guy 5 Diameter | Guy 5 Bearing | Guy 6 Assc. | Guy 6 Lead Length | Guy 6 Diameter | Guy 6 Bearing | Pole Number | Contractor Comments | Current Wind Rating | Proposed Work (If Applicable) | Estimated Cost | New Wind Rating | LAT / LONG DELTA (In Feet) | Horizontal Pole Loading % | OBJECTID | ID | STATUS | USAGE | MATERIAL | HEIGHT | CLASS | TREATMENT | KIP_RATING | DEPTH | GRADE | ESTIMATE_ | ACCESSIBLE | STRUCTURE | BRAND_DATE | ESTIMATED_ | INSTALL_DA | MANUFACTUR | OWNER_TYPE | OWNER_NAME | CRITICAL | FPL_ID | ATTACHMENT | LEVEL | ATTACHED_ | MAP_NUMBER | MANAGEMENT | SERVICE_CE | FRAN_NAME_ | FRAN_TYPE | ZIPCODE | COUNTY_NAM | CATV | PHONE | X_COORD | Y_COORD | FPL_ATT | POLE_LOAD | AMS_LAT | AMS_LONG | FDR | Lateral_Mi | Feeder_Mil | SUB | MA | SVC | SYSTEM_VOL | PHASING | PHASE_ROTA | POINT_X | POINT_Y
4655571 | [5 empty] | 40 | 3 Wood | 3ph-tan-xarm-8' 6" stl-35kv pt-e-6.0.1 f1 | 132' | 65' |  |  |  | TRAN 25 KVA | 2 |  | PVC U-GUARD 2" |  | 0 | [13 empty] | 0 | [13 empty] | 3 | 343 ACAR (15/4) | 3/0 AAAC (7) | [5 empty] | 168 | -80.2639 | [31 empty] | 113
4523571 | [5 empty] | 50 | 2 Wood | 3PH-TAN-Xarm-9' Wood-45KV PT Poly-E-6.0.0 F1 | 157' | 136' |  |  |  | TRAN 75 KVA | 2 |  |  |  | 1 |  | 22.32 | 1 | [10 empty] | 1 |  | 19.36 | 1.5 | [10 empty] | 3 | 568 ACAR (15/4) | 3/0 AAAC (7) | [5 empty] | 45 | -80.2612 | [31 empty] | 181
271965531 | [5 empty] | 40 | 3 Wood | *3ph-tan-tri-wood pole-45kv pt poly-e-21.0.0 f1 | 58' | 65' |  |  |  | TRAN 75 KVA | 4 |  | PVC U-GUARD 5" |  | 1 |  | 15 | 1.5 | [10 empty] | 1 |  | 14 | 1.5 | [10 empty] | 3 | 1/0 AAAC (7) | 2 AAAC (7) | 2 AAAC (7) | 2 |  |  |  | 135 | -80.2675 | [31 empty] | 218
3912495 | [5 empty] | 45 | 2 Wood | *3ph-tan-tri-hpb-35kv pt poly-e-21.0.0 f1 | 98' | 40' |  |  |  |  | 0 | Cobra Head - 2 ft |  |  | 1 |  | 19.36 | 1.5 | [10 empty] | 1 |  | 18.19 | 1 | [10 empty] | 3 | 343 ACAR (15/4) | 3/0 AAAC (7) | 1/0 AAAC (7) | 1 |  |  |  | 88 | -80.2623 | [31 empty] | 91
273823592 | [14 empty] | 0 |  |  |  | 0 | [13 empty] | 0 | [21 empty] | 196 | -80.27
4457187 | [5 empty] | 45 | 2 Wood | *3PH-SLK SP DE-5' 4" Stl-45KV PC Top Poly-E-29.0.0 F4A | 54' | 123' |  |  |  |  | 0 |  |  |  | 1 |  | 21.58 | 0.75 | [10 empty] | 0 | [13 empty] | 3 | 568 ACAR (15/4) Slack | 3/0 AAAC (7) Slack | [5 empty] | 12 | -80.2599 |  | 30' | 9/16" EHS | 268° | [27 empty] | 96
271965533 | [5 empty] | 40 | 3 Wood | *3ph-tan-tri-wood pole-45kv pt poly-e-21.0.0 f1 | 100' | 43' | 79' |  |  | TRAN 15 KVA | 4 |  | SHIELD 4" |  | 1 |  | 16.42 | 1.5 | [10 empty] | 0 |  | 15.08 | 0.75 | [10 empty] | 3 | 2 AAAC (7) | 4 AAAC (7) | [5 empty] | 131 | -80.2667 | [31 empty] | 132
350104770 | [5 empty] | 45 | 2 Wood | 3PH-DE-Xarm-9' Dbl Wood-45KV Susp Poly-E-9.0.0 F2 | 85' | 102' | 148' |  | 3PH-DE-Xarm-9' Dbl Wood-45KV Susp Poly-E-9.0.0 F2 |  | 0 |  | PVC U-GUARD 5" |  | 1 |  | 21 | 1.5 | 21 | 1.5 | [8 empty] | 1 |  | 20 | 1.5 | 20 | 1.5 | [8 empty] | 3 | 1/0 AAAC (7) | 1/0 AAAC (7) | [5 empty] | 138 | -80.2681 |  | 24' | 7/16" EHS | 0° |  | 24' | 7/16" EHS | 87° | [23 empty] | 62
350087792 | [5 empty] | 50 | 8.00 KIP CONC | *3ph-tan-xarm-8' 6" stl-45kv pt poly-e-6.0.0 f4 | 69' | 76' |  |  |  | 3-CO TRI-MOUNT BKT | 1 |  | PVC U-GUARD 5" |  | 1 |  | 17.85 | 0.75 | [10 empty] | 1 |  | 16.67 | 0.75 | [10 empty] | 3 | 343 ACAR (15/4) | 3/0 AAAC (7) |  | 1 | 6 AL DPX SEC |  |  | 106 | -80.2641 | [31 empty] | 64
4652625 | [5 empty] | 40 | 2 Wood | *3PH-TAN-Xarm-9' Wood-45KV PT Poly-E-6.0.0 F1 | 96' | 105' |  |  |  | TRAN 37.5 KVA | 1 |  |  |  | 1 |  | 21.83 | 1 | [10 empty] | 1 |  | 20.83 | 1.5 | [10 empty] | 3 | 1/0 HD CU (7) | 2 AAAC (7) | 2 AAAC (7) | 2 |  |  |  | 189 | -80.2689 | [31 empty] | 130
269159736 | [5 empty] | 45 | 3 Wood | *3PH-TAN-Xarm-5' 4" Stl-35KV PC Top Poly-E-6.0.1 F3 | 109' | 98' | 95' | 84' |  |  | 0 |  |  |  | 1 |  | 20.67 | 1 | 20.67 | 1 | [8 empty] | 1 |  | 17.75 | 1.5 | 19.5 | 1.25 | 19 | 1.25 | [6 empty] | 3 | 568 ACAR (15/4) | 3/0 AAAC (7) |  | 1 | 6 AL DPX SEC |  |  | 76 | -80.2619 |  | 25' | 7/16" EHS | 90° | [27 empty] | 155
350134068 | [5 empty] | 50 | 8.00 KIP CONC | 3ph-tan-xarm-8' 6" stl-35kv pt-e-6.0.1 f1 | 74' | 30' |  |  |  | TRAN 167 KVA | 3 |  |  |  | 1 |  | 19.17 | 1 | [10 empty] | 0 | [13 empty] | 3 | 1/0 AAAC (7) | 1/0 AAAC (7) |  | 1 | 6 AL DPX SEC |  |  | 58 | -80.2606 | [31 empty] | 114
273862391 | [14 empty] | 0 |  |  |  | 0 | [13 empty] | 0 | [21 empty] | 75 | -80.262
4771533 | [5 empty] | 45 | 3 Wood | 3PH-TAN-Xarm-9' Wood-35KV PT-E-6.0.0 F1 | 71' | 110' |  |  |  |  | 0 |  |  |  | 1 |  | 17.65 | 1 | [10 empty] | 1 |  | 16.38 | 1.5 | [10 empty] | 3 | 1/0 AAAC (7) | 1/0 AAAC (7) | 1/0 AAAC (7) | 2 |  |  |  | 79 | -80.2626 | [31 empty] | 112
273195660 | [14 empty] | 0 |  |  |  | 0 | [13 empty] | 0 | [21 empty] | 232 | -80.2713
273195662 | [14 empty] | 0 |  |  |  | 0 | [13 empty] | 0 | [21 empty] | 223 | -80.2701
6099405 | [5 empty] | 50 | 2 Wood | 3ph-tan-xarm-9' wood-45kv pt poly-e-6.0.0 f1 | 119' | 38' |  |  |  | TRAN 75 KVA | 3 |  |  |  | 1 |  | 19.5 | 1 | [10 empty] | 1 |  | 17.41 | 1.5 | [10 empty] | 3 | 568 ACAR (15/4) | 3/0 AAAC (7) | [5 empty] | 43 | -80.2604 | [31 empty] | 157
4547091 | [5 empty] | 35 | 4 Wood | *3PH-TAN-Xarm-8' 10" FG-45KV PT Poly-E-6.0.1 F1 | 151' | 101' | 37' | 33' |  | TRAN 75 KVA | 2 |  |  |  | 1 |  | 16.34 | 1.5 | 16.34 | 1 | [8 empty] | 1 |  | 15.06 | 1.25 | 15.06 | 0.75 | [8 empty] | 3 | 568 ACAR (15/4) | 3/0 AAAC (7) |  | 1 | 2 AL TPX Slack |  |  | 228 | -80.2708 | [31 empty] | 309
273862386 | [14 empty] | 0 |  |  |  | 0 | [13 empty] | 0 | [21 empty] | 67 | -80.2621
268040734 | [5 empty] | 40 | 6.00 KIP CONC | *3ph-de-xarm-5' 4" stl-35kv susp poly-e-11.0.0 f3 | 63' |  |  |  |  | 3-CO TRI-MOUNT BKT | 1 | Open Bottom - 4 ft | SHIELD 5" | COND 2" | 1 |  | 18.25 | 0.75 | [10 empty] | 0 | [13 empty] | 3 | 343 ACAR (15/4) | 3/0 AAAC (7) |  | 1 | 1/0 AL TPX Slack |  |  | 102 | -80.2641 |  | 15' | 7/16" EHS | 176° | [27 empty] | 72
350134055 | [5 empty] | 45 | 2 Wood | 3ph-tan-xarm-8' 6" stl-35kv pt-e-6.0.1 f1 | 30' | 128' |  |  |  | 3-CO, 3-LA TRI-MOUNT BKT | 1 |  | PVC U-GUARD 5" |  | 1 |  | 19.17 | 1 | [10 empty] | 0 | [13 empty] | 3 | 1/0 AAAC (7) | 1/0 AAAC (7) |  | 1 | 3/0 AL QPX LASHED SEC |  |  | 59 | -80.2606 | [31 empty] | 136
4655565 | [5 empty] | 45 | 3 Wood | *3ph-tan-mod tri-hpb-35kv pt-e-21.0.0 f1 alt | 147' | 122' | 188' | 130' | *3ph-tan-tri-wood pole-45kv pc hor-e-21.0.0 f1 |  | 0 |  | SHIELD 2" |  | 1 |  | 19.75 | 1 | [10 empty] | 1 |  | 18.8333 | 1.5 | [10 empty] | 3 | 3/0 AAAC (7) | 1/0 AAAC (7) | 2 AAAC (7) | 2 |  |  |  | 166 | -80.2639 | [31 empty] | 186
3912357 | [5 empty] | 45 | 3 Wood | 3PH-TAN-Tri-Wood Pole-45KV PC Hor-E-21.0.0 F1 | 237' | 216' | 68' | 110' |  | TRAN 50 KVA | 1 |  |  |  | 1 |  | 19.62 | 0.75 | 19.62 | 0.75 | [8 empty] | 1 |  | 18 | 0.75 | 18 | 1 | [8 empty] | 3 | 343 ACAR (15/4) | 3/0 AAAC (7) | [5 empty] | 149 | -80.264 | [31 empty] | 185
3912237 | [5 empty] | 45 | 2 Wood | 3ph-de-xarm-9' hd dbl wood-45kv susp poly-e-9.0.0 f2 | 30' | 49' |  |  |  | TRAN 50 KVA | 1 |  |  |  | 0 | [13 empty] | 0 | [13 empty] | 3 | 3/0 ACSR (6/1) | 1/0 AAAC (7) | [5 empty] | 117 | -80.2666 |  | 18' | 7/16" EHS | 263° | [27 empty] | 134
3912351 | [5 empty] | 40 | 6.00 KIP CONC | 3PH-DE-Xarm-5' 4" Stl-35KV Susp Poly-E-11.0.0 F3 | 65' |  |  |  |  | 3-CO TRI-MOUNT BKT | 1 |  | SHIELD 5" |  | 0 | [13 empty] | 1 |  | 17.17 | 0.25 | [10 empty] | 3 | 343 ACAR (15/4) | 3/0 AAAC (7) | [5 empty] | 101 | -80.2641 |  | 18' | 7/16" EHS | 357° | [27 empty] | 48
271825808 | [14 empty] | 0 |  |  |  | 0 | [13 empty] | 0 | [21 empty] | 152 | -80.2642
6099435 | [5 empty] | 45 | 4 Wood | 3PH-TAN-Xarm-9' Wood-45KV PT Poly-E-6.0.0 F1 | 84' | 17' |  |  |  | TRAN 50 KVA | 3 |  | SHIELD 5" |  | 1 |  | 20.33 | 0.75 | [10 empty] | 1 |  | 18.42 | 1.5 | [10 empty] | 3 | 568 ACAR (15/4) | 3/0 AAAC (7) | [5 empty] | 24 | -80.2601 | [31 empty] | 178
352078200 | [5 empty] | 45 | 1 Wood | 3PH-TAN-Xarm-8' 6" Stl-45KV PT Poly-E-6.0.0 F4 | 49' | 99' |  |  |  | TRAN 50 KVA | 2 |  |  |  | 1 |  | 16.33 | 0.75 | [10 empty] | 1 |  | 15.25 | 1.5 | [10 empty] | 3 | 1/0 AAAC (7) | 1/0 AAAC (7) |  | 1 | 1/0 AL TPX SEC |  |  | 141 | -80.2687 | [31 empty] | 117
322849207 | [5 empty] | 50 | 12.0 KIP CONC | *3PH-TAN-Xarm-8' 6" Stl-45KV PT Poly-E-6.0.1 F1 | 52' | 237' |  |  |  | REC 3 PHASE | 1 | Cobra Head - 6 ft |  |  | 1 |  | 19.71 | 0.75 | [10 empty] | 1 |  | 18.71 | 1 | [10 empty] | 3 | 343 ACAR (15/4) | 3/0 AAAC (7) | [5 empty] | 147 | -80.2641 | [31 empty] | 75
352078206 | [5 empty] | 45 | 1 Wood | 3PH-TAN-Xarm-8' 6" Stl-45KV PT Poly-E-6.0.0 F4 | 99' | 70' |  |  |  |  | 0 |  |  |  | 1 |  | 16.74 | 0.75 | [10 empty] | 1 |  | 15.38 | 1.5 | [10 empty] | 3 | 1/0 AAAC (7) | 1/0 AAAC (7) |  | 1 | 3/0 AL QPX LASHED SEC |  |  | 142 | -80.269 | [31 empty] | 90
6099429 | [5 empty] | 40 | 4 Wood | *3ph-tan-xarm-9' wood-35kv pt-e-6.0.0 f1 | 84' | 91' | 135' |  | *3ph-de-xarm-9' hd dbl wood-35kv susp poly-e-9.0.0 f2 | 3-LA | 1 |  |  |  | 1 |  | 19.75 | 0.75 | 19.75 | 0.25 | [8 empty] | 2 |  | 18.83 | 1.5 | 17.67 | 0.25 | 18.83 | 1.5 | [6 empty] | 3 | 568 ACAR (15/4) | 3/0 AAAC (7) | [5 empty] | 14 | -80.2601 |  | 18' | 1/2" AW | 88° |  | 15' | 9/16" EHS | 88° |  | 10' | 7/16" EHS | 180° | [19 empty] | 64
4652169 | [5 empty] | 40 | 2 Wood | *3PH-TAN-Xarm-9' Wood-45KV PT Poly-E-6.0.0 F1 | 103' | 102' |  |  |  |  | 0 |  |  |  | 1 |  | 20.6667 | 1.5 | [10 empty] | 1 |  | 19.6667 | 1 | [10 empty] | 3 | 1/0 HD CU (7) | 2 AAAC (7) | 2 AAAC (7) | 2 |  |  |  | 191 | -80.2695 | [31 empty] | 113
348946531 | [5 empty] | 55 | 8.00 KIP CONC | 3ph-de-xarm-8' 10" dbl fg-45kv susp poly-e-10.0.0 f3 | 43' | 108' | 206' | 218' | 3ph-tan-mod ver-conc pole-45kv pt poly-e-5.0.0 f2 |  | 0 |  |  |  | 0 |  | 23 | 0.75 | [10 empty] | 1 |  | 23 | 0.75 | 22 | 2 | [8 empty] | 3 | 343 ACAR (15/4) | 3/0 AAAC (7) | [5 empty] | 23 | -80.2621 | [31 empty] | 90
3983673 | [5 empty] | 45 | 6.00 KIP CONC | 3ph-de-xarm-5' 4" stl-35kv susp poly-e-11.0.0 f1 | 36' |  |  |  |  | 3Ø RISER / CO / LA ASSEMBLY | 1 |  | PVC U-GUARD 5" |  | 0 | [13 empty] | 1 |  | 17.33 | 0.25 | [10 empty] | 3 | 343 ACAR (15/4) Slack | 3/0 AAAC (7) Slack |  | 1 | 3/0 AL QPX SEC |  |  | 30 | -80.2601 | [31 empty] | 128
4741485 | [5 empty] | 45 | 3 Wood | 3PH-TAN-Tri-HPB-45KV PT Poly-E-21.0.0 F1 | 193' | 69' |  |  |  |  | 0 | Security Light |  |  | 1 |  | 20.59 | 0.75 | [10 empty] | 1 |  | 19.41 | 0.75 | [10 empty] | 3 | 343 ACAR (15/4) | 3/0 AAAC (7) | [5 empty] | 107 | -80.2641 | [31 empty] | 143
4523481 | [5 empty] | 45 | 3 Wood | 3PH-TAN-Xarm-9' Wood-35KV PT-E-6.0.0 F1 | 151' | 43' |  |  |  | TRAN 75 KVA (Bank) | 3 |  |  |  | 1 |  | 18.57 | 0.25 | [10 empty] | 1 |  | 17.92 | 1.5 | [10 empty] | 3 | 343 ACAR (15/4) | 3/0 AAAC (7) | 1/0 AAAC (7) | 3 |  |  |  | 21 | -80.2615 | [31 empty] | 264
4771311 | [5 empty] | 45 | 2 Wood | 3PH-DE-Xarm-8' 6" Stl-35KV Susp Poly-E-10.0.0 F1 | 218' | 88' | 73' |  |  | TRAN 25 KVA | 2 |  |  |  | 1 |  | 20 | 1 | [10 empty] | 0 |  | 17.42 | 1 | [10 empty] | 3 | 2 AAAC (7) | 2 AAAC (7) | [5 empty] | 115 | -80.2658 |  | 11' | 7/16" EHS | 270° | [27 empty] | 158
272270465 | [14 empty] | 0 |  |  |  | 0 | [13 empty] | 0 | [21 empty] | 71 | -80.2621
4782315 | [5 empty] | 45 | 1 Wood | 3ph-tan-xarm-8' 10" fg-45kv pt poly-e-6.0.1 f1 | 70' | 118' |  |  |  | TRAN 25 KVA | 1 |  |  |  | 0 | [13 empty] | 0 | [13 empty] | 3 | 1/0 HD CU (7) | 2 HD CU (7) | [5 empty] | 202 | -80.2699 |  | 20' | 7/16" EHS | 177° | [27 empty] | 70
271415980 | [14 empty] | 0 |  |  |  | 0 | [13 empty] | 0 | [21 empty] | 93 | -80.263
6276585 | [5 empty] | 45 | 4 Wood | 3ph-tan-xarm-9' wood-35kv pt-e-6.0.0 f1 | 33' | 88' |  |  |  |  | 0 |  |  |  | 1 |  | 19.17 | 1 | [10 empty] | 1 |  | 17.83 | 1.5 | [10 empty] | 3 | 1/0 AAAC (7) | 1/0 AAAC (7) | 1/0 AAAC (7) | 2 |  |  |  | 77 | -80.2622 | [31 empty] | 103
4456563 | [14 empty] | 0 |  |  |  | 0 | [13 empty] | 0 | [21 empty] | 121 | -80.265
4456443 | [5 empty] | 45 | 2 Wood | *3PH-TAN-Xarm-9' Wood-45KV PT Poly-E-6.0.0 F1 | 49' | 218' |  |  |  | 3-CO TRI-MOUNT BKT | 1 |  | PVC U-GUARD 5" |  | 1 |  | 21.5 | 0.75 | [10 empty] | 0 | [13 empty] | 3 | 3/0 ACSR (6/1) | 1/0 AAAC (7) | [5 empty] | 116 | -80.2664 | [31 empty] | 82
6099417 | [5 empty] | 45 | 3 Wood | *3PH-TAN-Mod Ver-Wood Pole-45KV PC Hor-E-5.0.0 F1 | 36' | 71' | 109' |  | *1PH-DE-Vert-45KV Susp Poly-E-5.1.0 F4 |  | 0 |  |  |  | 1 |  | 18.42 | 1 | 18.42 | 1 | [8 empty] | 1 |  | 17.42 | 1.5 | 17.42 | 1.25 | [8 empty] | 3 | 568 ACAR (15/4) | 3/0 AAAC (7) | [5 empty] | 4 | -80.2601 |  | 7' | 9/16" EHS | 87° | [27 empty] | 87
6533418 | [14 empty] | 0 |  |  |  | 0 | [13 empty] | 0 | [21 empty] | 186 | -80.268
4547433 | [5 empty] | 35 | 4 Wood | *3ph-tan-avian xarm-9' wood-35kv pt-e-31.1.1 | 99' | 106' |  |  |  | TRAN 50 KVA | 1 |  |  |  | 1 |  | 18 | 1 | [10 empty] | 1 |  | 16.42 | 1 | [10 empty] | 3 | 2 HD CU (7) | 4 HD CU (1) |  | 1 | 2 AL TPX Slack |  |  | 224 | -80.2702 | [31 empty] | 179
4549977 | [5 empty] | 40 | 5 Wood | *3ph-tan-tri-hpb-35kv pt poly-e-21.0.0 f1 | 67' | 35' | 94' |  | *3ph-tan-tri-hpb-35kv pt poly-e-21.0.0 f1 |  | 0 |  |  |  | 1 |  | 19.95 | 0.75 | 19.94 | 0.75 | [8 empty] | 1 |  | 18.45 | 0.75 | 18.45 | 0.75 | [8 empty] | 3 | 2 AAAC (7) | 2 AAAC (7) | 1/0 AAAC (7) | 3 |  |  |  | 108 | -80.2643 | [31 empty] | 146
5224773 | [5 empty] | 45 | 1 Wood | 3ph-tan-xarm-8' 6" stl-45kv pt poly-e-6.0.0 f4 | 46' | 99' |  |  |  | TRAN 50 KVA | 2 |  |  |  | 1 |  | 22 | 1.5 | [10 empty] | 0 | [13 empty] | 3 | 2 AAAC (7) Slack | 4 AAAC (7) Slack |  | 1 | 6 AL DPX Slack |  |  | 130 | -80.2664 |  | 9' | 7/16" EHS | 77° | [27 empty] | 86
325299001 | [5 empty] | 45 | 2 Wood | 3PH-TAN-Tri-HPB-35KV PT Poly-E-21.0.0 F1 | 81' | 61' |  |  |  | TRAN 50 KVA | 1 |  | PVC U-GUARD 2" |  | 0 | [13 empty] | 2 |  | 20 | 1.25 | 19 | 1 | [8 empty] | 3 | 343 ACAR (15/4) | 3/0 AAAC (7) | [5 empty] | 97 | -80.2637 | [31 empty] | 88
3703689 | [5 empty] | 40 | 3 Wood | *3PH-TAN-Xarm-9' Wood-35KV PT-E-6.0.0 F1 | 98' | 71' |  |  |  | TRAN 10 KVA | 2 |  |  |  | 1 |  | 17.3333 | 0.75 | [10 empty] | 1 |  | 19.25 | 0.75 | [10 empty] | 3 | 343 ACAR (15/4) | 3/0 AAAC (7) | [5 empty] | -80.2639 | 25.8408 | [31 empty] | 170
3900903 | [5 empty] | 45 | 3 Wood | * | 136' | 184' |  |  |  |  | 0 |  |  |  | 0 | [13 empty] | 0 | [13 empty] | 3 | 343 ACAR (15/4) | 3/0 AAAC (7) | [5 empty] | 164 | -80.2639 | [31 empty] | 110
352078264 | [8 empty] | 64' | 62' |  |  |  |  | 0 |  |  |  | 0 | [13 empty] | 0 |  | 19.4167 | 1.25 | 15.4167 | 1 | [16 empty] | 51 | -80.2623
4456731 | [5 empty] | 45 | 3 Wood | *3PH-TAN-Tri-HPB-45KV PT Poly-E-21.0.0 F1 | 64' | 62' |  |  |  | TRAN 50 KVA | 1 | Open Bottom - 2 ft |  |  | 0 | [13 empty] | 2 |  | 19.4167 | 1.25 | 15.4167 | 1 | [8 empty] | 3 | 343 ACAR (15/4) | 3/0 AAAC (7) | [5 empty] | 98 | -80.2639 | [31 empty] | 116
4456611 | [5 empty] | 40 | 4 Wood | 3ph-tan-tri-hpb-35kv pt-e-21.0.0 f1 | 95' | 96' |  |  |  |  | 0 | Open Bottom - 2 ft |  |  | 1 |  | 19.02 | 0.75 | [10 empty] | 1 |  | 16.88 | 0.75 | 15.5833 | 1 | [8 empty] | 3 | 2 AAAC (7) | 2 AAAC (7) | 1/0 AAAC (7) | 2 |  |  |  | 110 | -80.2646 |  | 15' | 5/16" EHS | 267° | [27 empty] | 194
6129993 | [5 empty] | 45 | 2 Wood | *3ph-tan-tri-hpb-45kv pt poly-e-21.0.0 f1 | 115' | 87' |  |  |  |  | 0 | Open Bottom - 2 ft | SHIELD 2" |  | 0 |  | 15.42 | 1 | [10 empty] | 2 |  | 16.5833 | 1.25 | 15.5833 | 1 | [8 empty] | 3 | 343 ACAR (15/4) | 3/0 AAAC (7) | 1/0 AAAC (7) | 3 |  |  |  | 96 | -80.2634 |  | 15' | 5/16" EHS | 267° | [27 empty] | 98
4480281 | [5 empty] | 45 | 1 Wood | 3ph-tan-mod ver-wood pole-45kv pt poly-e-5.0.0 f1 | 47' | 103' |  |  |  |  | 0 |  | SHIELD 2" |  | 1 |  | 15.42 | 1 | [10 empty] | 0 | [13 empty] | 3 | 1/0 AAAC (7) Slack | 1/0 AAAC (7) Slack |  | 1 | 6 AL DPX Slack |  |  | 56 | -80.2607 |  | 15' | 7/16" EHS | 358° | [27 empty] | 106
271416407 | [14 empty] | 0 |  |  |  | 0 | [13 empty] | 0 | [21 empty] | 103 | -80.2643
6275145 | [5 empty] | 40 | 3 Wood | *3ph-tan-tri-wood pole-45kv pt poly-e-21.0.0 f1 | 44' | 63' |  |  |  |  | 0 |  |  |  | 2 |  | 16.92 | 1.5 | 14.5 | 1 | [8 empty] | 0 | [13 empty] | 3 | 2 AAAC (7) | 4 AAAC (7) | [5 empty] | 132 | -80.2669 | [31 empty] | 268
270741654 | [8 empty] | 105' | 192' |  |  |  |  | 0 |  |  |  | 0 | [13 empty] | 0 | [21 empty] | 89 | -80.2623
4766031 | [5 empty] | 70 | 1 Wood | 3ph-tan-xarm-5' 4" stl-69kv pc top poly-e-6.0.1 f3 | 105' | 192' |  |  |  | TRAN 75 KVA | 2 |  | PVC U-GUARD 2" |  | 0 |  | 17.6667 | 1 | [10 empty] | 0 |  | 14 | 1.5 | [10 empty] | 3 | 568 ACAR (15/4) | 3/0 AAAC (7) | [5 empty] | 65 | -80.2619 | [31 empty] | 164
4654683 | [5 empty] | 40 | 3 Wood | 3ph-tan-xarm-9' wood-35kv pt-e-6.0.0 f1 | 103' | 79' |  |  |  | TRAN 50 KVA | 1 |  | PVC U-GUARD 2" |  | 1 |  | 17.6667 | 1 | [10 empty] | 1 |  | 14 | 1.5 | [10 empty] | 3 | 1/0 AAAC (7) | 2 AAAC (7) | 2 AAAC (7) Slack | 2 |  |  |  | 175 | -80.2652 | [31 empty] | 136
270741652 | [14 empty] | 0 |  |  |  | 0 | [13 empty] | 0 | [21 empty] | 91 | -80.2626
4549647 | [5 empty] | 35 | 5 Wood | 3ph-tan-xarm-9' wood-35kv pt-e-6.0.0 f1 | 103' | 103' |  |  |  |  | 0 | Security Light |  |  | 1 |  | 18 | 1 | [10 empty] | 1 |  | 15.3333 | 1.5 | [10 empty] | 3 | 3/0 AAAC (7) | 1/0 AAAC (7) | 2 AAAC (7) | 2 |  |  |  | 174 | -80.2649 | [31 empty] | 197
270741650 | [8 empty] | 106' | 101' |  |  |  |  | 0 |  |  |  | 0 |  | 16.7 | 1.5 | [10 empty] | 0 |  | 15.64 | 1 | [18 empty] | 95 | -80.2634
4547691 | [5 empty] | 35 | 3 Wood | *3ph-tan-xarm-9' wood-35kv pt-e-6.0.0 f1 | 106' | 101' |  |  |  | TRAN 37.5 KVA | 1 |  |  |  | 1 |  | 16.7 | 1.5 | [10 empty] | 1 |  | 15.64 | 1 | [10 empty] | 3 | 2 AAAC (7) | 2 AAAC (7) |  | 1 | 1/0 AL TPX Slack |  |  | 207 | -80.2696 |  | 30' | 7/16" EHS | 265° |  | 27' | 7/16" EHS | 265° |  | 24' | 5/16" EHS | 265° | [19 empty] | 157
4749945 | [5 empty] | 50 | 2 Wood | 3PH-DE-Xarm-9' HD Dbl Wood-45KV Susp Poly-E-9.0.0 F2 | 55' | 71' |  |  |  | TRAN 25 KVA | 3 | Open Bottom - 4 ft |  |  | 1 |  | 21.25 | 1 | [10 empty] | 1 |  | 19.1667 | 1.5 | [10 empty] | 3 | 568 ACAR (15/4) Slack | 3/0 AAAC (7) Slack |  | 1 | 1/0 AL TPX Slack |  |  | 47 | -80.2618 |  | 30' | 7/16" EHS | 265° |  | 27' | 7/16" EHS | 265° |  | 24' | 5/16" EHS | 265° | [19 empty] | 135
4614897 | [5 empty] | 40 | 3 Wood | 3PH-TAN-Xarm-9' Wood-45KV PT Poly-E-6.0.0 F1 | 93' | 80' |  |  |  |  | 0 |  |  |  | 1 |  | 18.3333 | 1 | [10 empty] | 1 |  | 17 | 1.5 | [10 empty] | 3 | 1/0 AAAC (7) |  |  | 1 | 1/0 AL TPX SEC |  |  | 182 | -80.267 | [31 empty] | 94
270741648 | [14 empty] | 0 |  |  |  | 0 | [13 empty] | 0 | [21 empty] | 146 | -80.2642
3912321 | [5 empty] | 45 | 3 Wood | 3ph-de-xarm-5' 4" stl-45kv susp poly-e-11.0.0 f1 | 175' | 115' | 175' | 65' |  | TRAN 50 KVA | 2 |  | PVC U-GUARD 2" |  | 1 |  | 20.58 | 1.5 | [10 empty] | 2 |  | 19.83 | 1.5 | 19 | 1.25 | 18 | 1 | 20.17 | 1.25 | 19.08 | 1 | 18 | 1 | 3 | 343 ACAR (15/4) Slack | 3/0 AAAC (7) Slack | [5 empty] | 120 | -80.2646 | [31 empty] | 242
350171282 | [5 empty] | 45 | 3 Wood | *3ph-de-xarm-8' 6" stl-45kv susp poly-e-10.0.0 f1 | 71' | 48' | 175' | 65' | * |  | 0 | Open Bottom - 2 ft | PVC U-GUARD 2" |  | 0 |  | 22 | 1.5 | [10 empty] | 3 |  | 20.17 | 1.25 | 19.08 | 1 | 18 | 1 | 20.17 | 1.25 | 19.08 | 1 | 18 | 1 | 3 | 343 ACAR (15/4) | 3/0 AAAC (7) | 2 AAAC (7) Slack | 2 |  |  |  | 99 | -80.2641 | [31 empty] | 212
3848511 | [5 empty] | 45 | 2 Wood | 3ph-tan-xarm-8' 6" stl-45kv pt poly-e-6.0.0 f4 | 102' | 46' | 99' |  |  |  | 0 |  |  |  | 1 |  | 22 | 1.5 | [10 empty] | 0 | [13 empty] | 3 | 1/0 AAAC (7) Slack | 1/0 AAAC (7) Slack | [5 empty] | 129 | -80.2663 | [31 empty] | 126
350128376 | [5 empty] | 45 | 2 Wood | *3PH-TAN-Xarm-8' 6" Stl-45KV PC Top Poly-E-6.0.1 F1 | 190' | 106' |  |  |  |  | 0 |  |  |  | 1 |  | 19 | 1 | [10 empty] | 0 |  | 19.41 | 0.25 | [10 empty] | 3 | 1/0 AAAC (7) | 1/0 AAAC (7) | [5 empty] | 52 | -80.2618 | [31 empty] | 89
354341041 | [5 empty] | 50 | 8.00 KIP CONC | 3ph-tan-xarm-8' 6" stl-45kv pc top poly-e-6.0.1 f1 | 130' | 204' |  |  |  | REC 3 PHASE | 1 |  |  |  | 0 | [13 empty] | 1 |  | 19.41 | 0.25 | [10 empty] | 3 | 1/0 HD CU (7) | 2 HD CU (7) | [5 empty] | 194 | -80.2698 | [31 empty] | 89
6275031 | [5 empty] | 40 | 3 Wood | 3ph-tan-tri-wood pole-45kv pt poly-e-21.0.0 f1 | 63' | 83' |  |  |  | TRAN 50 KVA | 4 | Security Light |  |  | 1 |  | 18.5833 | 1.5 | [10 empty] | 1 |  | 17.5833 | 1 | [10 empty] | 3 | 1/0 AAAC (7) | 2 AAAC (7) | 2 AAAC (7) | 2 |  |  |  | 133 | -80.2671 | [31 empty] | 154
4547577 | [5 empty] | 45 | 4 Wood | *3PH-TAN-Xarm-9' Wood-35KV PT-E-6.0.0 F1 | 118' | 104' | 103' | 108' | *3PH-TAN-Xarm-9' Wood-35KV PT-E-6.0.0 F1 | TRAN 37.5 KVA | 1 |  | PVC U-GUARD 2" |  | 0 |  | 20.92 | 1.5 | [10 empty] | 1 |  | 18.33 | 0.75 | [10 empty] | 3 | 1/0 HD CU (7) | 2 HD CU (7) |  | 1 | 6 AL DPX Slack |  |  | 201 | -80.2699 | [31 empty] | 179
3647481 | [5 empty] | 45 | 8.00 KIP CONC | 3ph-tan-tri-conc pole-45kv pc hor-e-21.0.0 f1 | 145' | 71' |  |  |  | 3Ø RISER / CO / LA ASSEMBLY | 1 |  | PVC U-GUARD 2" |  | 1 |  | 18.17 | 0.25 | [10 empty] | 1 |  | 15.25 | 1.5 | [10 empty] | 3 | 568 ACAR (15/4) | 3/0 AAAC (7) | [5 empty] | 1 | -80.2601 | [31 empty] | 73
5215833 | [14 empty] | 0 |  |  |  | 0 | [13 empty] | 0 | [21 empty] | 229 | -80.2709
270842971 | [8 empty] | 109' | 36' |  |  |  |  | 0 |  | PVC U-GUARD 2" |  | 0 |  | 22 | 0.75 | [10 empty] | 0 |  | 18.08 | 1 | [18 empty] | 162 | -80.2641 |  | 15' | 5/16" EHS | 178°
4439895 | [5 empty] | 45 | 4 Wood | 3ph-de-xarm-5' 4" stl-35kv susp poly-e-11.0.0 f1 | 109' | 36' |  |  |  | TRAN 10 KVA (Bank) | 3 |  | PVC U-GUARD 2" |  | 1 |  | 22 | 0.75 | [10 empty] | 1 |  | 18.08 | 1 | [10 empty] | 3 | 336 ACSR (18/1) | 3/0 ACSR (6/1) | [5 empty] | 29 | -80.2601 |  | 15' | 5/16" EHS | 178° | [27 empty] | 310
4655073 | [5 empty] | 35 | 4 Wood | 3ph-tan-xarm-9' wood-35kv pt-e-6.0.0 f1 | 121' | 103' |  |  |  | TRAN 37.5 KVA | 1 | Security Light | PVC U-GUARD 5" |  | 1 |  | 19.0833 | 1 | [10 empty] | 1 |  | 16.6667 | 1.5 | [10 empty] | 3 | 3/0 AAAC (7) | 1/0 AAAC (7) | 2 AAAC (7) | 2 |  |  |  | 173 | -80.2646 | [31 empty] | 208
4771521 | [5 empty] | 45 | 3 Wood | 3ph-tan-xarm-9' wood-35kv pt-e-6.0.0 f1 | 128' | 71' |  |  |  | TRAN 25 KVA | 1 |  | SHIELD 4" |  | 1 |  | 16.39 | 0.75 | [10 empty] | 1 |  | 14.63 | 1.5 | [10 empty] | 3 | 1/0 AAAC (7) | 1/0 AAAC (7) | 1/0 AAAC (7) | 2 |  |  |  | 80 | -80.2628 |  | 23' | 7/16" EHS | 260° | [27 empty] | 139
4721505 | [5 empty] | 45 | 2 Wood | 3PH-DE-Xarm-5' 4" Stl-45KV Susp Poly-E-11.0.0 F1 | 30' |  |  |  |  | 3Ø RISER / CO / LA ASSEMBLY | 1 |  | SHIELD 4" |  | 0 | [13 empty] | 0 | [13 empty] | 3 | 2 AAAC (7) | 2 AAAC (7) | [5 empty] | 118 | -80.2667 |  | 23' | 7/16" EHS | 260° | [27 empty] | 73
272301850 | [8 empty] | 210' | 103' |  |  |  |  | 0 |  |  |  | 0 |  | 21 | 1 | [10 empty] | 0 |  | 20 | 1 | [18 empty] | 195 | -80.27
3624231 | [5 empty] | 55 | 8.00 KIP CONC | 3PH-TAN-Xarm-8' 6" Stl-35KV PT Poly-E-6.0.1 F1 | 210' | 103' |  |  |  |  | 0 |  |  |  | 1 |  | 21 | 1 | [10 empty] | 1 |  | 20 | 1 | [10 empty] | 3 | 568 ACAR (15/4) | 3/0 AAAC (7) | [5 empty] | 49 | -80.262 | [31 empty] | 85
6275601 | [5 empty] | 40 | 4 Wood | *3PH-TAN-Tri-Wood Pole-45KV PT Poly-E-21.0.0 F1 | 90' | 65' |  |  |  | TRAN 15 KVA | 2 |  |  |  | 1 |  | 20.42 | 1 | [10 empty] | 1 |  | 19.33 | 1 | [10 empty] | 3 | 2 AAAC (7) | 2 AAAC (7) | [5 empty] | 114 | -80.2655 | [31 empty] | 123
3860859 | [5 empty] | 45 | 4 Wood | 3ph-tan-tri-hpb-35kv pt-e-21.0.0 f1 | 40' | 81' | 88' |  |  | TRAN 50 KVA | 1 | Cobra Head - 2 ft |  |  | 0 | [13 empty] | 2 |  | 18.73 | 1.25 | 16.62 | 0.75 | 17.62 | 1 | [6 empty] | 3 | 343 ACAR (15/4) | 3/0 AAAC (7) | 1/0 AAAC (7) | 1 |  |  |  | 90 | -80.2625 | [31 empty] | 163
270842966 | [14 empty] | 0 |  |  |  | 0 | [13 empty] | 0 | [21 empty] | 144 | -80.2693
4439883 | [14 empty] | 0 |  |  |  | 0 | [13 empty] | 0 | [21 empty] | 7 | -80.2601
5246895 | [14 empty] | 0 |  |  |  | 0 | [13 empty] | 0 | [21 empty] | 60 | -80.2605
6354597 | [5 empty] | 45 | 3 Wood | 3ph-tan-tri-wood pole-45kv pc hor-e-21.0.0 f1 | 216' | 106' | 156' |  |  | 3-CO TRI-MOUNT BKT | 2 | Cobra Head - 6 ft |  |  | 1 |  | 21.21 | 0.75 | 22 | 1.5 | [8 empty] | 1 |  | 19.69 | 0.75 | [10 empty] | 3 | 343 ACAR (15/4) | 3/0 AAAC (7) | [5 empty] | 150 | -80.264 | [31 empty] | 149
5226945 | [5 empty] | 50 | 8.00 KIP CONC | 3PH-DE-Xarm-8' 6" Stl-45KV Susp Poly-E-10.0.0 F1 | 102' | 44' | 156' |  |  |  | 0 |  | PVC U-GUARD 5" |  | 1 |  | 22 | 1.5 | 22 | 1.5 | [8 empty] | 0 |  | 18.45 | 1 | [10 empty] | 3 | 2 AAAC (7) Slack | 4 AAAC (7) Slack | [5 empty] | 128 | -80.266 | [31 empty] | 92
350087785 | [5 empty] | 50 | 8.00 KIP CONC | 3PH-TAN-Xarm-8' 6" Stl-45KV PT Poly-E-6.0.0 F4 | 48' | 52' |  |  |  | 3-CO TRI-MOUNT BKT | 1 |  | PVC U-GUARD 5" |  | 1 |  | 19.38 | 0.75 | [10 empty] | 1 |  | 18.45 | 1 | [10 empty] | 3 | 343 ACAR (15/4) | 3/0 AAAC (7) |  | 1 | 6 AL DPX SEC |  |  | 145 | -80.2641 | [31 empty] | 58
6016023 | [5 empty] | 40 | 4 Wood | 3PH-TAN-Tri-Wood Pole-45KV PT Poly-E-21.0.0 F1 | 83' | 58' | 191' | 151' |  | TRAN 50 KVA | 1 | Security Light |  |  | 1 |  | 17 | 1.5 | 22.75 | 1 | 22.75 | 1 | [6 empty] | 1 |  | 16 | 1 | 19.83 | 1 | 19.83 | 1 | [6 empty] | 3 | 1/0 AAAC (7) | 2 AAAC (7) | 2 AAAC (7) | 2 |  |  |  | 134 | -80.2673 | [31 empty] | 154
3543566 | [5 empty] | 55 | 2 Wood | 3ph-de-xarm-5' 4" stl-35kv susp poly-e-11.0.0 f1 | 96' | 92' | 191' | 151' |  |  | 0 |  |  |  | 1 |  | 22.75 | 1 | 22.75 | 1 | 22.75 | 1 | [6 empty] | 1 |  | 21 | 1.5 | 19.83 | 1 | 19.83 | 1 | [6 empty] | 3 | 568 ACAR (15/4) | 3/0 ACSR (6/1) | [5 empty] | 68 | -80.2619 | [31 empty] | 107
4654539 | [5 empty] | 40 | 3 Wood | 2PH-DE-Xarm-9' HD Dbl Wood-45KV Susp Poly-E-9.0.0 F2 NUET | 79' | 72' | 30' |  |  |  | 0 |  |  |  | 1 |  | 18.0833 | 1 | [10 empty] | 1 |  | 14.9167 | 1.5 | 16.58 | 0.75 | [8 empty] | 3 | 3/0 AAAC (7) | 1/0 AAAC (7) | [5 empty] | 176 | -80.2655 |  | 22' | 7/16" EHS | 267° |  | 25' | 7/16" EHS | 267° | [23 empty] | 109
4523601 | [5 empty] | 45 | 2 Wood | 3PH-TAN-Tri-HPB-35KV PT Poly-E-21.0.0 F1 | 111' | 148' | 30' |  |  | TRAN 50 KVA (Bank) | 2 | Open Bottom - 2 ft |  |  | 1 |  | 17.75 | 0.75 | [10 empty] | 1 |  | 16.58 | 1 | 16.58 | 0.75 | [8 empty] | 3 | 343 ACAR (15/4) | 3/0 AAAC (7) | 2 AAAC (7) | 3 |  |  |  | 85 | -80.2609 | [31 empty] | 135
4523721 | [5 empty] | 45 | 3 Wood | 3PH-TAN-Tri-Conc Pole-45KV PC Hor-E-21.0.0 F1 | 110' | 54' |  |  |  | TRAN 25 KVA | 2 |  | PVC U-GUARD 5" | PVC U-GUARD 5" | 1 |  | 18.17 | 1 | [10 empty] | 1 |  | 17.67 | 1.5 | [10 empty] | 3 | 568 ACAR (15/4) | 3/0 AAAC (7) | [5 empty] | 9 | -80.2601 | [31 empty] | 194
4439889 | [5 empty] | 45 | 3 Wood | 3PH-TAN-Xarm-9' Wood-35KV PT-E-6.0.0 F1 | 125' | 109' |  |  |  | 3Ø RISER / CO / LA ASSEMBLY | 2 | Cobra Head - 6 ft | PVC U-GUARD 5" | PVC U-GUARD 5" | 1 |  | 19.64 | 1 | [10 empty] | 1 |  | 18.04 | 1.5 | [10 empty] | 3 | 336 ACSR (18/1) | 3/0 AAAC (7) |  | 1 | 6 AL DPX SEC |  |  | 27 | -80.2601 | [31 empty] | 181
5770887 | [5 empty] | 40 | 2 Wood | *3PH-TAN-Tri-HPB-35KV PT Poly-E-21.0.0 F1 | 75' | 59' |  |  |  | TRAN 50 KVA | 1 |  |  |  | 1 |  | 18.38 | 0.75 | [10 empty] | 1 |  | 16.5 | 0.75 | [10 empty] | 3 | 2 AAAC (7) | 2 AAAC (7) | 1/0 AAAC (7) | 2 |  |  |  | 112 | -80.2651 | [31 empty] | 108
4548207 | [5 empty] | 40 | 4 Wood | 3PH-DE-Xarm-9' HD Dbl Wood-45KV Susp Poly-E-9.0.0 F2 | 100' | 58' |  |  |  | TRAN 37.5 KVA | 2 | Open Bottom - 2 ft |  |  | 1 |  | 17.36 | 0.75 | [10 empty] | 1 |  | 15.52 | 1 | [10 empty] | 3 | 2 AAAC (7) | 2 AAAC (7) | 2 AAAC (7) | 2 |  |  |  | 219 | -80.2682 | [31 empty] | 143
5241753 | [5 empty] | 70 | 1 Wood | 3ph-tan-xarm-5' 4" stl-69kv pc top poly-e-6.0.1 f3 | 92' | 105' |  |  |  |  | 0 |  |  |  | 0 | [13 empty] | 0 | [13 empty] | 3 | 568 ACAR (15/4) | 3/0 AAAC (7) | [5 empty] | 66 | -80.2619 | [31 empty] | 90
273801600 | [8 empty] | 150' | 105' | 91' |  |  |  | 0 |  |  |  | 0 |  | 19.86 | 0.25 | 19.86 | 1.5 | [8 empty] | 0 |  | 18.5 | 1.5 | 17.5 | 1.5 | 18.5 | 2 | [14 empty] | 28 | -80.2602
3920031 | [5 empty] | 50 | 8.00 KIP CONC | 3ph-de-xarm-8' 6" stl-45kv susp poly-e-10.0.0 f1 | 150' | 105' | 91' |  | 3ph-de-xarm-5' 4" stl-45kv susp poly-e-11.0.0 f1 | AT&T (16x30x31) | 1 |  |  |  | 1 |  | 19.86 | 0.25 | 19.86 | 1.5 | [8 empty] | 2 |  | 18.5 | 1.5 | 17.5 | 1.5 | 18.5 | 2 | [6 empty] | 3 | 343 ACAR (15/4) | 3/0 AAAC (7) | 1/0 AAAC (7) | 3 |  |  |  | 37 | -80.26 | [31 empty] | 156
4652349 | [5 empty] | 40 | 5 Wood | 3PH-TAN-Xarm-9' Wood-45KV PT Poly-E-6.0.0 F1 | 102' | 96' |  |  |  | TRAN 50 KVA | 1 | Security Light | COND 2" |  | 0 | [13 empty] | 2 |  | 19.25 | 1.25 | 16.5 | 1 | [8 empty] | 3 | 1/0 HD CU (7) | 2 AAAC (7) | 2 AAAC (7) | 2 |  |  |  | 190 | -80.2692 | [31 empty] | 210
350087830 | [5 empty] | 50 | 8.00 KIP CONC | 3PH-TAN-Xarm-8' 6" Stl-69KV PT Poly-E-6.0.1 F1 | 76' | 63' | 65' | 120' | *3PH-DE-Xarm-8' 6" Dbl Stl-45KV Susp Poly-E-10.0.0 F3 |  | 0 | Security Light | PVC U-GUARD 2" |  | 1 |  | 18 | 0.75 | 18 | 0.75 | [8 empty] | 1 |  | 17 | 0.75 | 17 | 0.5 | [8 empty] | 3 | 343 ACAR (15/4) | 3/0 AAAC (7) |  | 1 | 6 AL DPX SEC |  |  | 104 | -80.2641 |  | 22' | 7/16" EHS | 255° | [27 empty] | 82
5770275 | [5 empty] | 40 | 5 Wood | *3PH-TAN-Tri-Wood Pole-45KV PT Poly-E-21.0.0 F1 | 65' | 64' |  |  |  |  | 0 |  | PVC U-GUARD 2" |  | 1 |  | 15.67 | 1.5 | [10 empty] | 1 |  | 14.5 | 1.5 | [10 empty] | 3 | 1/0 AAAC (7) | 2 AAAC (7) | 2 AAAC (7) | 2 |  |  |  | 136 | -80.2677 |  | 22' | 7/16" EHS | 255° | [27 empty] | 123
4614861 | [5 empty] | 40 | 3 Wood | 3ph-tan-xarm-9' wood-45kv pt poly-e-6.0.0 f1 | 80' | 104' |  |  |  |  | 0 |  | COND 2" |  | 1 |  | 21.9167 | 1 | [10 empty] | 1 |  | 20.25 | 1.5 | [10 empty] | 3 | 1/0 AAAC (7) | 2 AAAC (7) | 1/0 AAAC (7) Slack | 2 |  |  |  | 184 | -80.2676 | [31 empty] | 148
272372190 | [8 empty] | 59' | 61' |  |  |  |  | 0 |  |  |  | 0 |  | 18.5833 | 0.75 | [10 empty] | 0 |  | 16.9167 | 0.75 | [18 empty] | 64 | -80.2621
5770833 | [5 empty] | 40 | 4 Wood | *3PH-TAN-Tri-HPB-35KV PT Poly-E-21.0.0 F1 | 59' | 61' |  |  |  |  | 0 |  |  |  | 1 |  | 18.5833 | 0.75 | [10 empty] | 1 |  | 16.9167 | 0.75 | [10 empty] | 3 | 2 AAAC (7) | 2 AAAC (7) | 1/0 AAAC (7) | 2 |  |  |  | 113 | -80.2653 | [31 empty] | 106
352078190 | [5 empty] | 45 | 2 Wood | 3PH-TAN-Xarm-8' 6" Stl-45KV PT Poly-E-6.0.0 F4 | 102' | 53' |  |  |  | TRAN 50 KVA | 2 |  |  |  | 1 |  | 21 | 0.75 | [10 empty] | 1 |  | 20 | 1.5 | [10 empty] | 3 | 1/0 AAAC (7) | 1/0 AAAC (7) |  | 1 | 1/0 AL TPX SEC |  |  | 139 | -80.2684 | [31 empty] | 127
4614975 | [5 empty] | 40 | 3 Wood | 3PH-TAN-OHGW-Xarm-9' Wood-45KV PT-E-18.1.1 F1 | 72' | 46' |  |  |  |  | 0 |  |  |  | 1 |  | 17.91 | 1 | [10 empty] | 1 |  | 16.16 | 1.5 | [10 empty] | 3 | 1/0 AAAC (7) | 2 AAAC (7) | 1/0 AAAC (7) | 2 |  |  |  | 177 | -80.2657 | [31 empty] | 82
6545814 | [8 empty] | 53' | 49' |  |  |  |  | 0 |  |  |  | 0 |  | 21 | 0.75 | [10 empty] | 0 |  | 20 | 1.5 | [18 empty] | 208 | -80.2693
352078195 | [5 empty] | 45 | 1 Wood | 3PH-TAN-Xarm-8' 6" Stl-45KV PT Poly-E-6.0.0 F4 | 53' | 49' |  |  |  | TRAN 50 KVA | 3 |  |  |  | 1 |  | 21 | 0.75 | [10 empty] | 1 |  | 20 | 1.5 | [10 empty] | 3 | 1/0 AAAC (7) | 1/0 AAAC (7) |  | 1 | 1/0 AL TPX SEC |  |  | 140 | -80.2686 | [31 empty] | 86
5241867 | [5 empty] | 50 | 2 Wood | 3ph-de-xarm-5' 4" stl-35kv susp poly-e-11.0.0 f1 | 79' | 96' |  |  |  |  | 0 |  |  |  | 1 |  | 21.18 | 1 | [10 empty] | 1 |  | 20 | 1.5 | 17.8333 | 1 | [8 empty] | 3 | 568 ACAR (15/4) | 3/0 AAAC (7) | [5 empty] | 69 | -80.2619 |  | 25' | 7/16" EHS | 180° |  | 28' | 9/16" EHS | 180° | [23 empty] | 95
4480353 | [5 empty] | 40 | 2 Wood | 3ph-slk sp de-9' dbl wood-35kv pc top-e-29.0.0 f1a | 105' | 43' |  |  |  |  | 0 | Cobra Head - 6 ft | PVC U-GUARD 2" |  | 1 |  | 19.8333 | 1.5 | [10 empty] | 2 |  | 18.8333 | 0.25 | 17.8333 | 1 | [8 empty] | 3 | 343 ACAR (15/4) | 3/0 AAAC (7) | 1/0 AAAC (7) | 3 |  |  |  | 41 | -80.26 |  | 25' | 7/16" EHS | 180° |  | 28' | 9/16" EHS | 180° | [23 empty] | 90
379688791 | [5 empty] | 40 | 2 Wood | *3ph-de-xarm-9' hd dbl wood-45kv susp poly-e-9.0.0 f2 | 151' | 43' |  |  |  | TRAN 75 KVA (Bank) | 3 |  | PVC U-GUARD 2" |  | 1 |  | 16.33 | 0.25 | [10 empty] | 0 | [13 empty] | 3 | 343 ACAR (15/4) | 3/0 AAAC (7) | [5 empty] | 22 | -80.262 |  | 22' | 7/16" EHS | 270° | [27 empty] | 141
PHID | [14 empty] | 0 |  |  |  | 0 | [13 empty] | 0 | [21 empty] | -80.2642 | 25.8432
354249707 | [14 empty] | 0 |  |  |  | 0 | [13 empty] | 0 | [21 empty] | 151 | -80.2642
354249705 | [14 empty] | 0 |  |  |  | 0 | [13 empty] | 0 | [21 empty] | 40 | -80.2598
4622949 | [5 empty] | 40 | 2 Wood | *3ph-tan-xarm-9' wood-45kv pt poly-e-6.0.0 f1 | 104' | 93' |  |  |  | TRAN 50 KVA | 1 |  | PVC U-GUARD 2" |  | 1 |  | 17.4167 | 1 | [10 empty] | 1 |  | 16.25 | 1.5 | [10 empty] | 3 | 1/0 AAAC (7) |  |  | 1 | 1/0 AL TPX SEC |  |  | 183 | -80.2673 | [31 empty] | 127
3912405 | [5 empty] | 45 | 2 Wood |  | 81' | 55' | 136' | 176' |  |  | 0 |  |  |  | 1 |  | 20.28 | 0.75 | [10 empty] | 1 |  | 19.08 | 1.5 | [10 empty] | 1 | 1/0 AAAC (7) | 1/0 AAAC (7) | 1/0 AAAC (7) | 2 |  |  |  | 160 | -80.2639 |  | 27' | 7/16" EHS | 180° | [27 empty] | 116
4655961 | [5 empty] | 40 | 2 Wood | *3PH-TAN-Xarm-9' Wood-35KV PT-E-6.0.0 F1 | 76' | 125' |  |  |  | TRAN 50 KVA | 1 |  |  |  | 1 |  | 17.75 | 0.75 | [10 empty] | 1 |  | 15.09 | 1 | [10 empty] | 3 | 1/0 AAAC (7) | 1/0 AAAC (7) | 1/0 AAAC (7) | 2 |  |  |  | 81 | -80.2632 | [31 empty] | 112
6099393 | [8 empty] | 103' | 129' |  |  |  |  | 0 |  |  |  | 0 |  | 22 | 1 | [10 empty] | 0 |  | 21 | 1 | [18 empty] | 84 | -80.2604
3906507 | [5 empty] | 50 | 2 Wood | 3ph-tan-xarm-9' wood-45kv pt poly-e-6.0.0 f1 | 103' | 129' |  |  |  | TRAN 75 KVA | 3 | Security Light |  |  | 1 |  | 22 | 1 | [10 empty] | 1 |  | 21 | 1 | [10 empty] | 3 | 568 ACAR (15/4) | 3/0 AAAC (7) | [5 empty] | 61 | -80.262 | [31 empty] | 257
272247365 | [14 empty] | 0 |  |  |  | 0 | [13 empty] | 0 | [21 empty] | 62 | -80.2621
4653777 | [5 empty] | 45 | 3 Wood | 3ph-tan-xarm-9' wood-45kv pt poly-e-6.0.0 f1 | 79' | 66' |  |  |  | TRAN 50 KVA | 1 |  |  |  | 1 |  | 18.75 | 1 | [10 empty] | 1 |  | 17 | 1.5 | [10 empty] | 3 | 1/0 AAAC (7) |  |  | 1 | 1/0 AL TPX SEC |  |  | 181 | -80.2668 | [31 empty] | 117
5247153 | [8 empty] | 110' | 33' |  |  |  |  | 0 |  | PVC U-GUARD 2" |  | 0 |  | 18.75 | 1 | [10 empty] | 0 |  | 17.42 | 1.5 | [18 empty] | 2 | -80.2603
4656369 | [5 empty] | 45 | 3 Wood | 3ph-tan-xarm-9' wood-35kv pt-e-6.0.0 f1 | 110' | 33' | 30' |  |  | TRAN 25 KVA | 1 |  | PVC U-GUARD 2" |  | 1 |  | 18.75 | 1 | [10 empty] | 1 |  | 17.42 | 1.5 | 15.83 | 0.75 | [8 empty] | 3 | 1/0 AAAC (7) | 1/0 AAAC (7) | 1/0 AAAC (7) | 2 |  |  |  | 78 | -80.2623 | [31 empty] | 95
4523511 | [5 empty] | 45 | 2 Wood | *3PH-TAN-Tri-HPB-35KV PT Poly-E-21.0.0 F1 | 148' | 221' | 30' |  |  | TRAN 50 KVA (Bank) | 3 |  |  |  | 1 |  | 17 | 0.75 | 17.27 | 1.5 | [8 empty] | 1 |  | 15.83 | 1 | 15.83 | 0.75 | [8 empty] | 3 | 343 ACAR (15/4) | 3/0 AAAC (7) | [5 empty] | 86 | -80.2614 | [31 empty] | 188
6362055 | [5 empty] | 45 | 3 Wood | 3ph-tan-xarm-9' wood-35kv pt-e-6.0.0 f1 | 131' | 55' |  |  |  | TRAN 37.5 KVA (Bank) | 2 | Security Light |  |  | 2 |  | 18.15 | 0.25 | 17.27 | 1.5 | [8 empty] | 1 |  | 16.46 | 1 | [10 empty] | 3 | 336 ACSR (18/1) | 3/0 ACSR (6/1) | 1/0 AAAC (7) | 3 |  |  |  | 35 | -80.26 | [31 empty] | 157
272340377 | [14 empty] | 0 |  |  |  | 0 | [13 empty] | 0 | [21 empty] | 163 | -80.2641
4655265 | [5 empty] | 40 | 3 Wood | 3PH-TAN-OHGW-Xarm-9' Wood-45KV PT-E-18.1.1 F1 | 122' | 121' |  |  |  | TRAN 50 KVA | 1 |  |  |  | 1 |  | 18 | 1 | [10 empty] | 1 |  | 17 | 1.5 | [10 empty] | 3 | 3/0 AAAC (7) | 1/0 AAAC (7) | 2 AAAC (7) | 2 |  |  |  | 172 | -80.2643 | [31 empty] | 161
4456041 | [5 empty] | 40 | 5 Wood | *3ph-tan-xarm-9' wood-35kv pt-e-6.0.0 f1 | 104' | 98' |  |  |  |  | 0 |  |  |  | 1 |  | 21.58 | 0.25 | [10 empty] | 1 |  | 19.49 | 0.25 | [10 empty] | 3 | 1/0 HD CU (7) | 2 HD CU (7) | [5 empty] | 199 | -80.2699 | [31 empty] | 100
3900897 | [5 empty] | 45 | 3 Wood | 3ph-tan-xarm-9' wood-45kv pt poly-e-6.0.0 f1 | 200' | 108' | 135' |  |  | 1-LA | 2 | Cobra Head - 6 ft |  |  | 1 |  | 20.58 | 1.5 | 21.4167 | 0.25 | [8 empty] | 1 |  | 19.33 | 0.75 | 19.5 | 0.75 | [8 empty] | 3 | 343 ACAR (15/4) | 3/0 AAAC (7) | [5 empty] | 156 | -80.264 |  | 20' | 1/2" AW | 359° |  | 26' | 7/16" EHS | 85° | [23 empty] | 182
4758069 | [5 empty] | 45 | 2 Wood | 3ph-de-xarm-5' 4" stl-35kv susp poly-e-11.0.0 f1 | 73' | 131' | 135' |  | 3ph-de-xarm-5' 4" stl-35kv susp poly-e-11.0.0 f1 |  | 0 | Security Light |  |  | 1 |  | 21.39 | 0.25 | 21.4167 | 0.25 | [8 empty] | 1 |  | 17.89 | 0.75 | 19.5 | 0.75 | [8 empty] | 3 | 336 ACSR (18/1) | 3/0 ACSR (6/1) |  | 1 | 2 AL TPX SEC |  |  | 33 | -80.26 |  | 20' | 1/2" AW | 359° |  | 26' | 7/16" EHS | 85° | [23 empty] | 76
3906513 | [5 empty] | 50 | 2 Wood | 3ph-tan-xarm-5' 4" stl-45kv pc top poly-e-6.0.1 f3 | 129' | 192' |  |  |  | TRAN 25 KVA | 1 |  |  |  | 1 |  | 24.25 | 1 | [10 empty] | 1 |  | 23.25 | 1 | [10 empty] | 3 | 568 ACAR (15/4) | 3/0 AAAC (7) |  | 1 | 2 AL TPX SEC |  |  | 63 | -80.262 | [31 empty] | 209
4456047 | [5 empty] | 45 | 4 Wood | *3PH-TAN-Xarm-9' Wood-45KV PT Poly-E-6.0.0 F1 | 98' | 130' |  |  |  |  | 0 |  |  |  | 1 |  | 21.8333 | 0.25 | [10 empty] | 0 | [13 empty] | 3 | 1/0 HD CU (7) | 2 HD CU (7) | [5 empty] | 198 | -80.2699 | [31 empty] | 143
272335901 | [8 empty] | 221' | 98' | 108' |  |  |  | 0 |  | COND 2" |  | 0 |  | 21 | 0.75 | [10 empty] | 0 |  | 21 | 0.75 | 20 | 1 | 20 | 1 | [14 empty] | 225 | -80.2704
3912507 | [5 empty] | 45 | 2 Wood | *3PH-TAN-Tri-HPB-35KV PT Poly-E-21.0.0 F1 | 221' | 98' | 108' |  |  | TRAN 37.5 KVA (Bank) | 4 |  | COND 2" |  | 0 |  | 21 | 0.75 | [10 empty] | 2 |  | 21 | 0.75 | 20 | 1 | 20 | 1 | [6 empty] | 3 | 343 ACAR (15/4) | 3/0 AAAC (7) | [5 empty] | 87 | -80.262 | [31 empty] | 155
5219811 | [8 empty] | 106' | 134' |  |  |  |  | 0 |  |  |  | 0 |  | 19.17 | 1 | [10 empty] | 0 | [21 empty] | 212 | -80.2688
4395129 | [5 empty] | 50 | 2 Wood | 3PH-TAN-Mod Ver-Wood Pole-45KV PT Poly-E-5.0.0 F1 | 106' | 134' |  |  |  |  | 0 |  | PVC U-GUARD 2" |  | 1 |  | 19.17 | 1 | [10 empty] | 0 |  | 15.5833 | 1.5 | [10 empty] | 3 | 1/0 AAAC (7) | 1/0 AAAC (7) | [5 empty] | 53 | -80.2614 | [31 empty] | 73
6128379 | [5 empty] | 40 | 4 Wood | 3PH-TAN-Tri-Wood Pole-45KV PT Poly-E-21.0.0 F1 | 64' | 85' |  |  |  | TRAN 37.5 KVA | 3 |  | PVC U-GUARD 2" |  | 1 |  | 16.5 | 1.5 | [10 empty] | 1 |  | 15.5833 | 1.5 | [10 empty] | 3 | 1/0 AAAC (7) | 1/0 AAAC (7) | [5 empty] | 137 | -80.2679 | [31 empty] | 105
5247261 | [8 empty] | 136' | 119' |  |  |  |  | 0 |  |  |  | 0 |  | 19.67 | 1 | [10 empty] | 0 |  | 14.25 | 1.5 | [18 empty] | 26 | -80.2602
4523643 | [5 empty] | 50 | 2 Wood | 3ph-tan-xarm-9' wood-45kv pt poly-e-6.0.0 f1 | 136' | 119' |  |  |  | TRAN 75 KVA | 3 |  |  |  | 1 |  | 19.67 | 1 | [10 empty] | 1 |  | 14.25 | 1.5 | [10 empty] | 3 | 568 ACAR (15/4) | 3/0 AAAC (7) | [5 empty] | 44 | -80.2607 | [31 empty] | 194
4614825 | [5 empty] | 40 | 5 Wood | 3ph-tan-xarm-9' wood-45kv pt poly-e-6.0.0 f1 | 105' | 94' |  |  |  |  | 0 |  |  |  | 1 |  | 19.42 | 1 | 16.52 | 1.5 | [8 empty] | 1 |  | 16.42 | 1.5 | [10 empty] | 3 | 1/0 HD CU (7) | 2 AAAC (7) | 2 AAAC (7) | 2 |  |  |  | 188 | -80.2686 | [31 empty] | 216
3868251 | [5 empty] | 45 | 3 Wood | 3ph-tan-xarm-9' wood-35kv pt-e-6.0.0 f1 | 55' | 148' | 220' | 220' |  | CAP 1200 KVAR | 1 | Security Light |  |  | 2 |  | 17.61 | 0.25 | 16.52 | 1.5 | [8 empty] | 1 |  | 15.63 | 1 | [10 empty] | 3 | 336 ACSR (18/1) | 3/0 ACSR (6/1) | 1/0 AAAC (7) | 3 |  |  |  | 36 | -80.26 | [31 empty] | 146
4744887 | [5 empty] | 50 | 2 Wood | 3PH-DE-Xarm-5' 4" Stl-45KV Susp Poly-E-11.0.0 F1 | 55' | 211' | 220' | 220' |  | TRAN 25 KVA | 4 |  |  |  | 1 |  | 21.42 | 1 | [10 empty] | 1 |  | 20.33 | 1.5 | [10 empty] | 3 | 568 ACAR (15/4) Slack | 3/0 AAAC (7) Slack |  | 1 | 1/0 AL TPX Slack |  |  | 48 | -80.262 | [31 empty] | 341
6130101 | [5 empty] | 50 | 3 Wood | *3ph-tan-tri-hpb-45kv pt poly-e-21.0.0 f1 | 122' | 59' | 115' |  | *3ph-tan-tri-hpb-45kv pt poly-e-21.0.0 f1 | TRAN 100 KVA (Bank) | 4 | Open Bottom - 2 ft |  |  | 0 |  | 21.33 | 1 | [10 empty] | 2 |  | 20 | 1.25 | 19 | 1 | 20 | 1.25 | 19 | 1 |  |  |  |  | 3 | 343 ACAR (15/4) | 3/0 AAAC (7) | 1/0 AAAC (7) | 3 |  |  |  | 94 | -80.2631 | [31 empty] | 214
5241951 | [5 empty] | 45 | 3 Wood | 3ph-tan-xarm-9' wood-45kv pt poly-e-6.0.0 f1 | 109' | 109' |  |  |  |  | 0 |  | SHIELD 3" | SHIELD 3" | 1 |  | 21.33 | 1 | [10 empty] | 1 |  | 20.17 | 1.5 | [10 empty] | 3 | 568 ACAR (15/4) | 3/0 AAAC (7) | [5 empty] | 72 | -80.2619 |  | 20' | 7/16" EHS | 180° | [27 empty] | 130
78275597 | [5 empty] | 45 | 4 Wood | 3ph-de-xarm-9' hd dbl wood-35kv susp poly-e-9.0.0 f2 | 48' | 90' |  |  |  | TRAN 25 KVA | 1 |  | SHIELD 3" | SHIELD 3" | 1 |  | 19.6 | 1 | [10 empty] | 1 |  | 18.4 | 1.5 | [10 empty] | 3 | 568 ACAR (15/4) | 3/0 AAAC (7) | 2 AAAC (7) | 2 |  |  |  | 13 | -80.2601 |  | 20' | 7/16" EHS | 180° | [27 empty] | 269
6130227 | [5 empty] | 45 | 3 Wood | *3ph-tan-tri-wood pole-45kv pt poly-e-21.0.0 f1 | 122' | 81' |  |  |  |  | 0 | Open Bottom - 2 ft |  |  | 0 | [13 empty] | 2 |  | 16.07 | 1.25 | 14.75 | 1 | [8 empty] | 3 | 343 ACAR (15/4) | 3/0 AAAC (7) | 1/0 AAAC (7) | 3 |  |  |  | 92 | -80.2627 | [31 empty] | 141
3541790 | [14 empty] | 0 |  |  |  | 0 | [13 empty] | 0 | [21 empty] | 234 | -80.2719
5893479 | [8 empty] | 103' | 74' |  |  |  |  | 0 |  | PVC U-GUARD 5" | PVC U-GUARD 5" | 0 |  | 20.67 | 1 | [10 empty] | 0 | [21 empty] | 153 | -80.2642
239520010 | [5 empty] | 50 | 8.00 KIP CONC | 3PH-TAN-Xarm-8' 6" Stl-35KV PT-E-6.0.1 F1 | 103' | 74' |  |  |  | 3Ø RISER / CO / LA ASSEMBLY | 2 | Cobra Head - 6 ft | PVC U-GUARD 5" | PVC U-GUARD 5" | 1 |  | 20.67 | 1 | [10 empty] | 0 | [13 empty] | 3 | 1/0 AAAC (7) | 1/0 AAAC (7) |  | 1 | 6 AL DPX SEC |  |  | 57 | -80.2606 | [31 empty] | 62
3741849 | [5 empty] | 45 | 3 Wood | 3ph-tan-xarm-9' wood-45kv pt poly-e-6.0.0 f1 | 95' | 151' | 150' |  |  |  | 0 |  |  |  | 1 |  | 21.5833 | 1 | [10 empty] | 1 |  | 17.9167 | 1.5 | [10 empty] | 3 | 1/0 AAAC (7) | 2 AAAC (7) | 1/0 AAAC (7) | 2 |  |  |  | 179 | -80.2663 | [31 empty] | 137
5241945 | [5 empty] | 45 | 3 Wood | 3ph-tan-xarm-5' 4" stl-35kv pc top poly-e-6.0.1 f3 | 109' | 109' |  |  |  |  | 0 |  | COND 2" |  | 1 |  | 21.17 | 1 | [10 empty] | 1 |  | 19.67 | 1.5 | [10 empty] | 3 | 568 ACAR (15/4) | 3/0 AAAC (7) | [5 empty] | 74 | -80.2619 | [31 empty] | 129
268907528 | [5 empty] | 40 | 2 Wood | *3ph-tan-xarm-9' wood-45kv pt poly-e-6.0.0 f1 | 48' | 81' |  |  |  | TRAN 25 KVA | 1 |  | COND 2" |  | 1 |  | 18.5833 | 1 | [10 empty] | 1 |  | 17 | 1.5 | [10 empty] | 3 | 1/0 HD CU (7) | 2 AAAC (7) | [5 empty] | 185 | -80.2678 | [31 empty] | 117
273860171 | [8 empty] | 73' | [5 empty] | 0 |  | SHIELD 5" | PVC U-GUARD 2" | 0 |  | 16.0833 | 0.25 | [10 empty] | 0 |  | 15.5833 | 0.75 | [18 empty] | 7 | -80.2603
4046505 | [5 empty] | 45 | 6.00 KIP CONC | 3ph-de-xarm-5' 4" stl-35kv susp poly-e-11.0.0 f1 | 73' | 43' |  |  |  | 3Ø RISER / CO / LA ASSEMBLY | 1 |  | SHIELD 5" | PVC U-GUARD 2" | 1 |  | 16.0833 | 0.25 | [10 empty] | 1 |  | 15.5833 | 0.75 | [10 empty] | 3 | 343 ACAR (15/4) Slack | 3/0 AAAC (7) Slack |  | 1 | 2 AL TPX SEC |  |  | 32 | -80.26 | [31 empty] | 185
4395135 | [5 empty] | 45 | 3 Wood | *3PH-TAN-Xarm-9' Wood-35KV PT-E-6.0.0 F1 | 93' | 43' |  |  |  | TRAN 50 KVA | 3 |  |  |  | 1 |  | 17.17 | 0.25 | [10 empty] | 1 |  | 16.5 | 1.5 | [10 empty] | 3 | 343 ACAR (15/4) | 3/0 AAAC (7) | 1/0 AAAC (7) | 3 |  |  |  | 20 | -80.2614 | [31 empty] | 157
-99973 | [14 empty] | 0 |  |  |  | 0 | [13 empty] | 0 | [21 empty] | 171 | -80.264
-99974 | [14 empty] | 0 |  |  |  | 0 | [13 empty] | 0 | [21 empty] | 155 | -80.2642
-99975 | [8 empty] | 96' | 92' | 130' | 124' |  |  | 0 |  |  |  | 0 |  | 20.5 | 1 | 20.5 | 1 | [8 empty] | 0 |  | 17.17 | 1.5 | 18.5833 | 1.5 | [16 empty] | 119 | -80.2642
4656573 | [5 empty] | 45 | 3 Wood | 3ph-tan-xarm-9' wood-45kv pt poly-e-6.0.0 f1 | 96' | 92' | 130' | 124' |  | TRAN 50 KVA | 1 |  |  |  | 1 |  | 20.5 | 1 | 20.5 | 1 | [8 empty] | 1 |  | 17.17 | 1.5 | 18.5833 | 1.5 | [8 empty] | 3 | 568 ACAR (15/4) | 3/0 AAAC (7) | [5 empty] | 70 | -80.2619 | [31 empty] | 184
273823563 | [14 empty] | 0 |  |  |  | 0 | [13 empty] | 0 | [21 empty] | 3 | -80.2603
-99976 | [14 empty] | 0 |  |  |  | 0 | [13 empty] | 0 | [21 empty] | 122 | -80.2653
-99977 | [14 empty] | 0 |  |  |  | 0 | [13 empty] | 0 | [21 empty] | 124 | -80.2654
-99978 | [14 empty] | 0 |  |  |  | 0 | [13 empty] | 0 | [21 empty] | 50 | -80.2622
-99979 | [8 empty] | 48' | 54' | 54' |  |  |  | 0 |  |  |  | 0 |  | 18.58 | 1 | 18.58 | 0.75 | [8 empty] | 0 |  | 17.33 | 1.5 | [18 empty] | 210 | -80.2692
78275589 | [5 empty] | 45 | 4 Wood | 3PH-DE-Xarm-9' HD Dbl Wood-35KV Susp Poly-E-9.0.0 F2 | 48' | 54' | 54' |  | 3PH-SLK SP DE-9' Dbl Wood-45KV PC Top Poly-E-29.0.0 F1A |  | 0 | Cobra Head - 6 ft |  |  | 1 |  | 18.58 | 1 | 18.58 | 0.75 | [8 empty] | 1 |  | 17.33 | 1.5 | [10 empty] | 3 | 568 ACAR (15/4) | 3/0 AAAC (7) | 2 AAAC (7) | 2 |  |  |  | 10 | -80.2601 | [31 empty] | 129
4456581 | [5 empty] | 40 | 4 Wood | *3ph-tan-tri-hpb-35kv pt-e-21.0.0 f1 | 96' | 75' |  |  |  |  | 0 | Security Light |  |  | 1 |  | 18.3333 | 0.75 | [10 empty] | 1 |  | 17.3333 | 0.75 | [10 empty] | 3 | 2 AAAC (7) | 2 AAAC (7) | 1/0 AAAC (7) | 2 |  |  |  | 111 | -80.2649 | [31 empty] | 113
273823564 | [14 empty] | 0 |  |  |  | 0 | [13 empty] | 0 | [21 empty] | 16 | -80.2603
273801599 | [8 empty] | 92' | 100' | 58' | 58' |  |  | 0 |  |  |  | 0 |  | 18.0833 | 0.75 | [10 empty] | 0 |  | 15.8333 | 1 | 15.8333 | 0.75 | [16 empty] | 170 | -80.264
3860595 | [5 empty] | 40 | 3 Wood | *3ph-tan-xarm-9' wood-35kv pt-e-6.0.0 f1 | 92' | 100' | 58' | 58' |  | TRAN 75 KVA | 1 |  |  |  | 1 |  | 18.0833 | 0.75 | [10 empty] | 1 |  | 15.8333 | 1 | 15.8333 | 0.75 | [8 empty] | 3 | 2 AAAC (7) | 2 AAAC (7) | 2 AAAC (7) | 2 |  |  |  | 217 | -80.2685 | [31 empty] | 126
4614939 | [5 empty] | 45 | 4 Wood | 3PH-TAN-Xarm-9' Wood-45KV PT Poly-E-6.0.0 F1 | 66' | 95' |  |  |  |  | 0 |  |  |  | 1 |  | 17.5833 | 1 | [10 empty] | 1 |  | 14.25 | 1.5 | [10 empty] | 3 | 1/0 AAAC (7) | 2 AAAC (7) | 1/0 AAAC (7) Slack | 2 |  |  |  | 180 | -80.2666 | [31 empty] | 106
4439829 | [5 empty] | 50 | 2 Wood | 3PH-TAN-Xarm-9' Wood-45KV PT Poly-E-6.0.0 F1 | 71' | 157' |  |  |  | TRAN 75 KVA | 3 |  |  |  | 1 |  | 23.25 | 1 | [10 empty] | 1 |  | 19.17 | 1.5 | [10 empty] | 3 | 568 ACAR (15/4) | 3/0 AAAC (7) | [5 empty] | 46 | -80.2616 | [31 empty] | 173
3951933 | [5 empty] | 45 | 2 Wood | *3PH-TAN-Xarm-9' Wood-35KV PT-E-6.0.0 F1 | 130' | 130' | 105' | 103' | *3PH-DE-Xarm-8' 10" Dbl FG-45KV Susp Poly-E-10.0.0 F3 | TRAN 50 KVA | 1 |  | PVC U-GUARD 2" |  | 0 |  | 21.25 | 1 | [10 empty] | 1 |  | 21.25 | 0.25 | [10 empty] | 3 | 1/0 HD CU (7) | 2 HD CU (7) | 2 HD CU (7) Slack | 2 |  |  |  | 192 | -80.2698 | [31 empty] | 112
3978639 | [8 empty] | 164' | 38' |  |  |  |  | 0 |  |  |  | 0 |  | 19.75 | 0.25 | [10 empty] | 0 |  | 18.58 | 1.5 | [18 empty] | 230 | -80.2713
4523667 | [5 empty] | 45 | 3 Wood | 3ph-tan-xarm-9' dbl wood-35kv pc top-e-6.0.0 f2 | 164' | 38' |  |  |  |  | 0 | Open Bottom - 4 ft |  |  | 1 |  | 19.75 | 0.25 | [10 empty] | 1 |  | 18.58 | 1.5 | [10 empty] | 3 | 568 ACAR (15/4) | 3/0 AAAC (7) | 2 AAAC (7) | 3 |  |  |  | 18 | -80.2606 | [31 empty] | 260
6533472 | [14 empty] | 0 |  |  |  | 0 | [13 empty] | 0 | [21 empty] | 203 | -80.2699
4652895 | [5 empty] | 40 | 5 Wood | 3PH-TAN-Xarm-9' Wood-45KV PT Poly-E-6.0.0 F1 | 94' | 111' |  |  |  | TRAN 50 KVA | 1 |  | PVC U-GUARD 2" | PVC U-GUARD 2" | 1 |  | 18.75 | 1 | [10 empty] | 1 |  | 16.9167 | 1.5 | [10 empty] | 3 | 1/0 HD CU (7) | 2 AAAC (7) | 2 AAAC (7) | 2 |  |  |  | 187 | -80.2683 |  | 16' | 7/16" EHS | 266° |  | 12' | 7/16" EHS | 266° | [23 empty] | 265
5218149 | [5 empty] | 45 | 2 Wood | 3PH-DE-Xarm-8' 6" Stl-45KV Susp Poly-E-10.0.0 F1 | 70' | 27' |  |  |  | 3-CO TRI-MOUNT BKT | 2 |  | PVC U-GUARD 5" |  | 1 |  | 17.26 | 0.75 | [10 empty] | 1 |  | 16.18 | 1.5 | [10 empty] | 3 | 1/0 AAAC (7) | 1/0 AAAC (7) |  | 1 | 1/0 AL TPX SEC |  |  | 143 | -80.2692 |  | 16' | 7/16" EHS | 266° |  | 12' | 7/16" EHS | 266° | [23 empty] | 70
-99984 | [14 empty] | 0 |  |  |  | 0 | [13 empty] | 0 | [21 empty] | 197 | -80.2703
3912399 | [5 empty] | 45 | 2 Wood | *3PH-DE-Xarm-9' Dbl Wood-45KV Susp Poly-E-9.0.0 F1 NUET | 176' | 204' | 123' | 127' |  |  | 0 |  |  |  | 0 |  | 20.13 | 0.75 | [10 empty] | 0 |  | 19.26 | 1.25 | [10 empty] | 3 | 343 ACAR (15/4) | 3/0 AAAC (7) | [5 empty] | 158 | -80.2639 | [31 empty] | 134
-99985 | [5 empty] | 45 | 4 Wood | 3PH-TAN-Xarm-9' Wood-45KV PT Poly-E-6.0.0 F1 | 117' | 17' |  |  |  | TRAN 25 KVA | 3 |  |  |  | 1 |  | 21.42 | 0.75 | [10 empty] | 1 |  | 20.17 | 1.5 | [10 empty] | 3 | 568 ACAR (15/4) | 3/0 AAAC (7) |  | 1 | 6 AL DPX Slack |  |  | 25 | -80.2601 | [31 empty] | 307
-99986 | [14 empty] | 0 |  |  |  | 0 | [13 empty] | 0 | [21 empty] | 169 | -80.264
4614969 | [5 empty] | 45 | 2.60 KIP CONC | 3ph-tan-tri-conc pole-45kv pc hor-e-21.0.0 f1 | 46' | 151' | 150' |  |  |  | 0 |  |  |  | 1 |  | 20.4167 | 1 | [10 empty] | 0 | [13 empty] | 3 | 1/0 AAAC (7) | 2 AAAC (7) | 1/0 AAAC (7) | 2 |  |  |  | 178 | -80.2658 |  | 20' | 7/16" EHS | 356° |  | 18' | 7/16" EHS | 356° | [23 empty] | 67
-99987 | [14 empty] | 0 |  |  |  | 0 | [13 empty] | 0 | [21 empty] | 161 | -80.2641
-99988 | [8 empty] | 150' | 88' |  |  |  |  | 0 |  | COND 2" |  | 0 |  | 17.13 | 0.75 | [10 empty] | 0 |  | 14.78 | 1 | [18 empty] | 148 | -80.2642
4550373 | [5 empty] | 40 | 4 Wood | *3PH-DE-Xarm-9' Dbl Wood-35KV Susp Poly-E-9.0.0 F2 | 150' | 88' |  |  |  |  | 0 |  | COND 2" |  | 1 |  | 17.13 | 0.75 | [10 empty] | 1 |  | 14.78 | 1 | [10 empty] | 3 | 1/0 AAAC (7) | 1/0 AAAC (7) | 1/0 AAAC (7) | 2 |  |  |  | 82 | -80.2634 |  | 26' | 7/16" EHS | 88° | [27 empty] | 175
3703701 | [5 empty] | 40 | 2 Wood | *3ph-de-xarm-9' hd dbl wood-45kv susp poly-e-9.0.0 f2 | 70' | 87' |  |  |  | Horz Gang Switch | 1 |  |  |  | 1 |  | 18.41 | 0.75 | [10 empty] | 1 |  | 15.03 | 0.75 | [10 empty] | 3 | 343 ACAR (15/4) | 3/0 AAAC (7) |  | 1 | 2 AL TPX Slack |  |  | 236 | -80.2722 |  | 26' | 7/16" EHS | 88° | [27 empty] | 164
-99989 | [14 empty] | 0 |  |  |  | 0 | [13 empty] | 0 | [21 empty] | 83 | -80.2603
6533460 | [14 empty] | 0 |  |  |  | 0 | [13 empty] | 0 | [21 empty] | 220 | -80.2681
3912393 | [5 empty] | 55 | 2 Wood | 3PH-TAN-Xarm-9' Wood-45KV PT Poly-E-6.0.0 F1 | 123' | 134' | 204' | 110' | *3PH-TAN-Xarm-8' 6" Stl-35KV PT-E-6.0.1 F1 NUET | Control Box | 1 |  |  |  | 1 |  | 20 | 0.75 | [10 empty] | 1 |  | 21.67 | 0.75 | [10 empty] | 1 | 2 AAAC (7) | 2 AAAC (7) | 2 AAAC (7) | 2 |  |  |  | 157 | -80.264 | [31 empty] | 208
272337734 | [14 empty] | 0 |  |  |  | 0 | [13 empty] | 0 | [21 empty] | 159 | -80.2641
273823575 | [14 empty] | 0 |  |  |  | 0 | [13 empty] | 0 | [21 empty] | 165 | -80.2641
-99980 | [14 empty] | 0 |  |  |  | 0 | [13 empty] | 0 | [21 empty] | 126 | -80.2659
271965510 | [14 empty] | 0 |  |  |  | 0 | [13 empty] | 0 | [21 empty] | 109 | -80.2644
-99981 | [14 empty] | 0 |  |  |  | 0 | [13 empty] | 0 | [21 empty] | 218 | -80.2682
-99982 | [14 empty] | 0 |  |  |  | 0 | [13 empty] | 0 | [21 empty] | 222 | -80.2679
-99983 | [8 empty] | 134' | 87' |  |  |  |  | 0 |  |  |  | 0 |  | 20.25 | 1 | [10 empty] | 0 | [21 empty] | 233 | -80.2718
4480227 | [5 empty] | 50 | 8.00 KIP CONC | 3ph-tan-mod ver-wood pole-45kv pt poly-e-5.0.0 f1 | 134' | 87' |  |  |  | CAP 1200 KVAR | 1 | Cobra Head - 6 ft |  |  | 1 |  | 20.25 | 1 | [10 empty] | 0 | [13 empty] | 3 | 1/0 AAAC (7) | 1/0 AAAC (7) |  | 1 | 6 AL DPX SEC |  |  | 54 | -80.261 |  | 18' | 7/16" EHS | 88° | [27 empty] | 61
350134083 | [5 empty] | 45 | 1 Wood | 3PH-TAN-Mod Ver-Wood Pole-45KV PT Poly-E-5.0.0 F1 | 87' | 47' |  |  |  |  | 0 |  |  |  | 1 |  | 17.33 | 1 | [10 empty] | 0 |  | 19 | 1.5 | [10 empty] | 3 | 1/0 AAAC (7) | 1/0 AAAC (7) |  | 1 | 6 AL DPX SEC |  |  | 55 | -80.2608 |  | 18' | 7/16" EHS | 88° | [27 empty] | 116
4523559 | [5 empty] | 45 | 3 Wood | *3PH-TAN-Xarm-9' Dbl Wood-35KV PC Top-E-6.0.0 F2 | 164' | 38' |  |  |  | TRAN 50 KVA | 3 |  |  |  | 1 |  | 20 | 0.25 | [10 empty] | 1 |  | 19 | 1.5 | [10 empty] | 3 | 568 ACAR (15/4) | 3/0 AAAC (7) | 2 AAAC (7) | 3 |  |  |  | 19 | -80.2611 | [31 empty] | 258
4523679 | [5 empty] | 45 | 3 Wood | 3PH-TAN-Xarm-9' Wood-35KV PT-E-6.0.0 F1 | 135' | 38' |  |  |  | TRAN 37.5 KVA | 3 | Security Light |  |  | 1 |  | 20 | 0.25 | [10 empty] | 1 |  | 19 | 1.5 | [10 empty] | 3 | 568 ACAR (15/4) | 3/0 AAAC (7) | 2 AAAC (7) | 3 |  |  |  | 17 | -80.2605 | [31 empty] | 221
6533466 | [14 empty] | 0 |  |  |  | 0 | [13 empty] | 0 | [21 empty] | 226 | -80.2705
-99995 | [14 empty] | 0 |  |  |  | 0 | [13 empty] | 0 | [21 empty] | 206 | -80.2696
-99996 | [14 empty] | 0 |  |  |  | 0 | [13 empty] | 0 | [21 empty] | 237 | -80.2723
273823584 | [14 empty] | 0 |  |  |  | 0 | [13 empty] | 0 | [21 empty] | 200 | -80.2701
-99997 | [14 empty] | 0 |  |  |  | 0 | [13 empty] | 0 | [21 empty] | 238 | -80.2724
-99998 | [8 empty] | 49' | 108' | 30' | 30' |  |  | 0 |  |  |  | 0 |  | 20.4 | 1.5 | [10 empty] | 0 |  | 18.79 | 1 | 18.75 | 0.75 | [16 empty] | 6 | -80.2605
4547871 | [5 empty] | 40 | 3 Wood | *3ph-tan-xarm-9' wood-35kv pt-e-6.0.0 f1 | 49' | 108' | 30' | 30' |  |  | 0 |  |  |  | 1 |  | 20.4 | 1.5 | [10 empty] | 1 |  | 18.79 | 1 | 18.75 | 0.75 | [8 empty] | 3 | 2 AAAC (7) | 2 AAAC (7) | [5 empty] | 211 | -80.2691 | [31 empty] | 107
273823580 | [14 empty] | 0 |  |  |  | 0 | [13 empty] | 0 | [21 empty] | 31 | -80.2602
3912381 | [5 empty] | 45 | 3 Wood | 3PH-TAN-Tri-Wood Pole-45KV PC Hor-E-21.0.0 F1 | 106' | 200' | 57' | 137' |  | 1-LA | 2 | Open Bottom - 2 ft |  |  | 1 |  | 23.22 | 1.5 | 23.22 | 0.25 | 21.94 | 0.75 | [6 empty] | 1 |  | 21.45 | 0.75 | 21.45 | 0.75 | [8 empty] | 3 | 343 ACAR (15/4) | 3/0 AAAC (7) | [5 empty] | 154 | -80.264 | [31 empty] | 214
-99990 | [14 empty] | 0 |  |  |  | 0 | [13 empty] | 0 | [21 empty] | 123 | -80.2654
-99991 | [14 empty] | 0 |  |  |  | 0 | [13 empty] | 0 | [21 empty] | 125 | -80.2655
-99992 | [14 empty] | 0 |  |  |  | 0 | [13 empty] | 0 | [21 empty] | 127 | -80.266
-99993 | [14 empty] | 0 |  |  |  | 0 | [13 empty] | 0 | [21 empty] | 73 | -80.2621
-99994 | [8 empty] | 38' | 90' |  |  |  |  | 0 |  |  |  | 0 |  | 19.22 | 1 | [10 empty] | 0 |  | 15.83 | 1.5 | [18 empty] | 216 | -80.2687 |  | 21' | 5/16" EHS | 90° |  | 25' | 9/16" EHS | 90°
241064398 | [5 empty] | 50 | 2 Wood | *3ph-tan-xarm-5' 4" stl-35kv pc top-e-6.0.1 f3 | 38' | 90' |  |  |  |  | 0 |  |  |  | 1 |  | 19.22 | 1 | [10 empty] | 1 |  | 15.83 | 1.5 | [10 empty] | 3 | 568 ACAR (15/4) | 3/0 AAAC (7) | [5 empty] | 42 | -80.2603 |  | 21' | 5/16" EHS | 90° |  | 25' | 9/16" EHS | 90° | [23 empty] | 138
6533454 | [14 empty] | 0 |  |  |  | 0 | [13 empty] | 0 | [21 empty] | 213 | -80.2688